## Sheet1
210 MLD SEWAGE TREATMENT PLANT,BINGAWAN,KANPURMONTHLY FLOW & LAB REPORT
Date | INLET FLOW in MLD | Plant Run In HRS | RAW SEWAGE | [5 empty] | AFTER UASB REACTOR | [5 empty] | FINAL OUTLET | [5 empty] | Sludge Concentration | FECAL COLIFORM (<1000) | POWER SHUTDOWN |  | REMARK
|  |  | Temp | TDS | PH(7-8) | COD(520mg/L) | BOD(320mg/L) | TSS(600mg/L) | Temp | TDS | PH | COD | BOD | TSS | Temp | TDS | PH(7-8) | COD(<100mg/L) | BOD(<30mg/L) | TSS(<50mg/L)
|  |  | c | ppm | ppm | ppm | ppm | ppm | c | ppm | ppm | ppm | ppm | ppm | c | ppm | ppm | ppm | ppm | ppm | % |  | HRS | MINS
2023-01-01 | 128.1 | 24 | 20 | 980 | 7.1 | 528 | 165 | 450 | 20 | 970 | 6.9 | 224 | 69 | 210 | 19 | 950 | 7.3 | 176 | 51 | 70 | 30.34 | 222000
2023-01-02 | 105.54 | 24 | 19 | 970 | 7.1 | 504 | 160 | 425 | 19 | 960 | 6.9 | 208 | 66 | 205 | 19 | 940 | 7.3 | 160 | 50 | 62 | 33.38 | 360750 | 6 | 15 | Power failure from Kesco Side
2023-01-03 | 133.67 | 24 | 19 | 910 | 7.1 | 520 | 165 | 420 | 19 | 890 | 6.9 | 216 | 69 | 200 | 18 | 870 | 7.3 | 168 | 53 | 60 | 32.05 | 360750
2023-01-04 | 134.52 | 24 | 19 | 930 | 7.2 | 544 | 175 | 433 | 19 | 900 | 7 | 232 | 72 | 210 | 18 | 890 | 7.4 | 184 | 55 | 64 | 30.72 | 222000
2023-01-05 | 132.27 | 24 | 18 | 950 | 7.2 | 536 | 170 | 450 | 18 | 960 | 6.9 | 304 | 87 | 216 | 18 | 930 | 7.4 | 208 | 60 | 80 | 32.09 | 152625
2023-01-06 | 134.52 | 24 | 18 | 980 | 7.2 | 560 | 190 | 440 | 18 | 990 | 6.9 | 320 | 96 | 207 | 17 | 950 | 7.4 | 232 | 64 | 76 | 32.49 | 222000
2023-01-07 | 127.06 | 24 | 17 | 970 | 7.1 | 552 | 185 | 423 | 16 | 990 | 6.9 | 312 | 90 | 196 | 16 | 960 | 7.3 | 216 | 61 | 84 | 31.01 | 152625
2023-01-08 | 83.84 | 24 | 17 | 960 | 7.1 | 528 | 170 | 437 | 17 | 980 | 6.9 | 296 | 87 | 200 | 16 | 940 | 7.3 | 224 | 63 | 92 | 34.3 | 77700 | 8 | 50 | Power failure from Kesco Side
2023-01-09 | 139.04 | 24 | 17 | 950 | 7.1 | 540 | 180 | 430 | 17 | 960 | 6.9 | 300 | 90 | 193 | 16 | 940 | 7.3 | 220 | 62 | 88 | 31.6 | 222000
2023-01-10 | 140.6 | 24 | 16 | 980 | 7.2 | 536 | 175 | 433 | 16 | 950 | 7 | 288 | 90 | 197 | 16 | 930 | 7.4 | 208 | 60 | 90 | 32.83 | 360750
2023-01-11 | 126.02 | 24 | 16 | 970 | 7.1 | 552 | 185 | 443 | 16 | 960 | 6.9 | 264 | 84 | 190 | 16 | 950 | 7.4 | 200 | 58 | 86 | 34 | 360750
2023-01-12 | 120.29 | 24 | 16 | 1000 | 7.1 | 520 | 165 | 440 | 16 | 980 | 6.9 | 280 | 90 | 203 | 16 | 960 | 7.4 | 216 | 61 | 92 | 32.28 | 222000
2023-01-13 | 121.85 | 24 | 17 | 980 | 7.1 | 544 | 175 | 445 | 17 | 960 | 6.9 | 288 | 90 | 205 | 16 | 940 | 7.4 | 208 | 60 | 88 | 32.03 | 152625
2023-01-14 | 132.79 | 24 | 17 | 960 | 7.1 | 528 | 160 | 420 | 17 | 970 | 6.9 | 304 | 93 | 213 | 17 | 950 | 7.3 | 224 | 62 | 94 | 32.16 | 77700
2023-01-15 | 126.02 | 24 | 17 | 940 | 7.2 | 504 | 155 | 413 | 17 | 930 | 7 | 272 | 81 | 200 | 17 | 910 | 7.3 | 200 | 57 | 82 | 31.78 | 83250
2023-01-16 | 129.31 | 24 | 16 | 950 | 7.2 | 536 | 170 | 427 | 16 | 970 | 7 | 288 | 87 | 203 | 16 | 930 | 7.4 | 216 | 61 | 90 | 31.06 | 152625
2023-01-17 | 127.94 | 24 | 16 | 920 | 7.2 | 520 | 165 | 410 | 16 | 940 | 6.9 | 304 | 93 | 216 | 15 | 910 | 7.4 | 224 | 65 | 96 | 31.07 | 360750
2023-01-18 | 132.79 | 24 | 16 | 940 | 7.2 | 488 | 155 | 350 | 16 | 920 | 6.9 | 280 | 87 | 196 | 15 | 900 | 7.5 | 224 | 64 | 80 | 30.74 | 222000
2023-01-19 | 143.72 | 24 | 16 | 930 | 7.1 | 504 | 160 | 400 | 16 | 910 | 6.9 | 320 | 96 | 203 | 15 | 890 | 7.4 | 256 | 70 | 88 | 31.35 | 152625
2023-01-20 | 131.05 | 24 | 17 | 960 | 7.1 | 560 | 185 | 387 | 17 | 940 | 6.9 | 272 | 87 | 210 | 16 | 940 | 7.4 | 208 | 63 | 106 | 30.07 | 83250
2023-01-21 | 142 | 24 | 17 | 950 | 7.1 | 544 | 175 | 380 | 17 | 960 | 6.9 | 256 | 81 | 193 | 16 | 930 | 7.3 | 192 | 60 | 100 | 31.62 | 77700
2023-01-22 | 132.44 | 24 | 16 | 940 | 7.1 | 552 | 180 | 453 | 16 | 960 | 6.9 | 296 | 93 | 194 | 16 | 920 | 7.3 | 216 | 65 | 113 | 31.11 | 65590
2023-01-23 | 141.48 | 24 | 16 | 970 | 7.1 | 528 | 170 | 433 | 16 | 950 | 6.9 | 312 | 96 | 220 | 16 | 950 | 7.3 | 224 | 70 | 110 | 31.09 | 83250
2023-01-24 | 138 | 24 | 16 | 960 | 7.2 | 560 | 185 | 420 | 16 | 930 | 7 | 320 | 99 | 207 | 16 | 920 | 7.4 | 232 | 72 | 102 | 31.5 | 83250
2023-01-25 | 133.31 | 24 | 17 | 1010 | 7.2 | 536 | 175 | 425 | 17 | 1000 | 6.9 | 280 | 87 | 204 | 17 | 970 | 7.4 | 208 | 65 | 98 | 30.96 | 111000
2023-01-26 | 119.77 | 24 | 17 | 1040 | 7.2 | 520 | 170 | 413 | 17 | 1020 | 6.9 | 264 | 81 | 200 | 16 | 1000 | 7.4 | 200 | 62 | 96 | 30.12 | 77700
2023-01-27 | 63.34 | 24 | 17 | 1000 | 7.2 | 528 | 170 | 396 | 17 | 980 | 6.9 | 248 | 78 | 193 | 16 | 950 | 7.4 | 192 | 60 | 90 | 31.15 | 111000 | 14 | 30 | Power failure from Kesco Side
2023-01-28 | 56.41 | 24 | 17 | 1020 | 7.2 | 496 | 155 | 400 | 17 | 1030 | 6.9 | 240 | 75 | 186 | 16 | 1000 | 7.5 | 184 | 57 | 86 | 30.39 | 152625 | 24 | 0
2023-01-29 | 65.78 | 24 | 17 | 1050 | 7.1 | 512 | 165 | 410 | 17 | 1050 | 7 | 224 | 72 | 183 | 17 | 1020 | 7.4 | 176 | 55 | 82 | 30.68 | 222000 | 24 | 0
2023-01-30 | 51.55 | 24 | 18 | 1010 | 7.1 | 480 | 155 | 383 | 18 | 1020 | 6.9 | 216 | 69 | 170 | 17 | 980 | 7.4 | 160 | 51 | 70 | 30.41 | 222000 | 24 | 0
2023-01-31 | 38.36 | 24 | 18 | 1030 | 7.1 | 504 | 160 | 397 | 18 | 1040 | 6.9 | 232 | 75 | 186 | 17 | 1000 | 7.4 | 184 | 56 | 80 | 30.72 | 152625 | 24 | 0
TOTAL | [22 empty] | 126 | 35
AVG | 117.21 | 24 | 17.1 | 971.29 | 7.14 | 527.87 | 170 | 418.9 | 17.06 | 966.77 | 6.92 | 272.9 | 84.19 | 200.29 | 16.52 | 942.58 | 7.37 | 204.52 | 60.42 | 86.94 | 31.52 | 179984.35